Job Hazard Analysis

Personal Protective Equipment Required:

| Task/Equipment: | Cleaning and Winterizing Cooling Tower |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin & Bryana Borders |
| Date: | 4/12/19 |

Rubber Boots

Slip Resistant

Chemical Resistant Gloves Gloves

Full Face Respirator

Heavy Leather Gloves

Waterproof Coveralls

Trainings Required*/ Recommended:

Hazardous communication*, ladder safety, eye safety, respirator use

Equipment/Tools/Chemicals Required for the Job:

Goodway TFC-200 machine, Goodway Scalebreak-Gel, Scalebreak neutralizer, 6-ft  ladder, hand tools, PH meter

| Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Turn tower fan control off at tower control panel. Open main power disconnect to cooling tower and secure with lockout protocol | No hazards present | N/A |
| - Open both North and South fan disconnect at cooling tower and secure with lock out protocol | No hazards present | N/A |
| - Isolate make-up water to tower by closing the 2 inch make-up ball valve | Ladder fall | Proper ladder use training |
| - Connect Scalebreak chemical drum to TCH-200 machine per manufacture’s instruction | Chemical inhalation, chemical splash, chemical skin contact, chemical eye contact, Slip and fall | Properly wear a full face respirator, chemical resistant gloves and protective coveralls |
| - Apply Scalebreak chemical to cooling tower fill using manufacturer’s directions and allow to set for 1 hour. | Chemical inhalation, chemical splash, chemical skin contact, chemical eye contact, slip and fall | Properly wear a full face respirator, chemical resistant gloves, rubber boots, wear protective coveralls |
| - Use Goodway TCH-200 machine to wash tower fill per manufacturer’s instructions | Chemical inhalation, chemical splash, chemical skin contact, chemical eye contact, slip and fall | Properly wear a full face respirator, chemical resistant gloves and protective coveralls |
| - Add scale break neutralizer chemical to tower basin per manufacturer’s instructions to neutralize basin water | Chemical inhalation, chemical splash, chemical skin contact, chemical eye contact, slip and fall | Properly wear a full face respirator, chemical resistant gloves, rubber boots and protective coveralls |
| - After PH has dropped (use PH meter) to acceptable levels ,open tower drain valve and allow sump basin to drain completely | Chemical contact with hands, eye, and skin. Slip and fall | Properly wear a full face respirator, chemical resistant gloves, rubber boots and protective coveralls |
| - Post another person outside the tower, enter using a six foot ladder and remove screen-strainers from sump suction | Ladder fall, finger cuts | Use proper ladder use protocol, wear heavy leather gloves |
| - Remove screens and clean with garden hose | Wet feet and hands could cause a loss of grip and a slip and fall | Use water proof gloves and rubber boots |
| - Sweep out all loose scale, dirt and debris from floor of cooling tower and dispose of | Slip and fall, wet surface | Use rubber boots |
| - Leave drain valve open to prevent freeze-up over the winter months | No hazards present | N/A |

Additional Information: Two person task

Safety Glasses

Lab Coat

Fall Protection Harness

High Vis Vest

Dust Mask

Hard Hat

Ear Protection