Job Hazard Analysis

| Task/Equipment: | Removal of Burner, Summer Boiler |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin & Bryana Borders |
| Date: | 4/12/19 |

Personal Protective Equipment Required:

Heavy Leather Gloves

Hard Hat

Trainings Required*/Recommended:

Proper ladder use*, OSHA 10

Equipment/Tools/Chemicals Required for the Job:

Hand wrench, washers, nuts, pipe wrench, screw driver, ladder and flash light

| Tasks/Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Open main power disconnects, and turn off control switch at burner panel. Secure using lockout tag out protocol | No hazards present | N/A |
| - Shut off main gas valves (2) and shut off pilot gas valve. Secure with lock-out tag-out protocol | No hazards present | N/A |
| - Attach chain fall to burner housing and support burner | Ladder fall | Proper ladder use |
| - Disconnect Gas line from burner at union | No hazards present | N/A |
| - Loosen and remove hex nuts holding burner to mounting flange | Finger pinch | Use heavy leather gloves |
| - Disconnect and remove gas pressure switch and store in a safe place | No hazards present | N/A |
| - Remove main flame and pilot scanner and secure | No hazards present | N/A |
| - Disconnect all pilot lines and set aside | No hazards present | N/A |
| - Remove all vent lines and set aside | Ladder fall | Proper ladder use |
| - Remove burner support stanchion and set aside | Falling objects | Stay clear and position an assistant to operate chain fall |
| - Remove gas recirculation piping and set aside | Ladder fall | Proper ladder use |
| - Remove burner muffler and set aside | No hazards present | N/A |
| - Move burner back from boiler along support-rail flame | Falling object | Stay from under burner at all times |
| - Inspect furnace and combustion chamber | Ladder fall | Proper ladder use |
| - Cordon off area with red caution tape | Falling objects | Stay clear |

Additional Information:

- This is a two person task

Lab Coat

Protection Suit

Fall Protection Harness

High Vis Vest

Safety Shoes

Splash Goggles

Cryogenic Gloves

Dust Mask

Respirator

Face Shield

Safety Glasses

Ear Protection