Job Hazard Analysis

| Task/Equipment: | Filter/Separator Change on Control Air Compressors |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin & Bryana Borders |
| Date: | 4/16/19 |

Personal Protective Equipment Required

Personal Protective Equipment Required

Hard Hat

Hard Hat

Safety Glasses

Safety Glasses

Heavy Leather Gloves

Heavy Leather Gloves

Trainings Required*/Recommended:

Lock out tag out*

Equipment/Tools/Chemicals Required for the Job:

Socket wrench, screw driver, filter wrenches, hand tools, funnel, oil/fluid absorbing compound; absorbent floor compound (optional)

| Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Start standby compressor | No hazards present | N/A |
| - check to insure water flow to drain from water-cooled standby compressor or cooling fan is running for air cooled compressor | Finger cuts and water splash-back into eyes | Wear leather gloves and eye protection |
| - Push stop button on control pad to stop compressor when being serviced | No hazards present | N/A |
| - Open main power disconnect at 3-phase distribution panel and secure using lock-out tag-out protocol | Skipping this step could cause major injury in step 6 + 7 | Lock-out tag-out procedure |
| - Isolate the compressor pneumatically and relieve system of air pressure until control panel pressure indicator reads zero | Skipping this step could cause serious face and eye injury in step 6 + 7 | Close and secure pneumatic pressure isolation valve using lock-out protocol .Verify that all system pressure has been dissipated before opening system to service. Wear safety googles and heavy leather gloves |
| - Open fluid filter drain valve to release fluid from filter rack | Eye or facial injury , skin burns from contact with hot fluid | Verify that all system pressure has been dissipated before opening system to service. Wear safety googles and heavy leather gloves |
| - Remove the filter/separator to be replaced using the filter wrench and hand tools | Eye or facial injury , skin burns from contact with hot fluid | Verify that all system pressure has been dissipated before opening system to service. Wear safety googles and heavy leather gloves |
| - Install new filter/separator and secure | No hazards present | N/A |
| - Close filter rack drain valve | Skin burns due to contact with hot surface | Wear heavy leather gloves |
| - Remove reservoir cap and visually check fluid level in sump. Add fluid if necessary | Skin burn due to contact with hot surfaces | Wear heavy leather gloves |
| - Replace reservoir cap and secure | Skin burns due to contact with hot surface | Wear heavy leather gloves |
| - Check for leaks around work area and filter/separator | Slip and fall | Mop up and clean any spills or fluid residue in work area. Apply absorbent floor compound to area if necessary |

Additional Information:

Lab Coat

Lab Coat

Protection Suit

Protection Suit

Fall Protection Harness

Fall Protection Harness

High Vis Vest

High Vis Vest

Safety Shoes

Safety Shoes

Splash Goggles

Splash Goggles

Cryogenic Gloves

Cryogenic Gloves

Latex Gloves

Latex Gloves

Dust Mask

Dust Mask

Respirator

Respirator

Hard Hat

Hard Hat

Face Shield

Face Shield

Safety Glasses

Safety Glasses

Ear Protection

Ear Protection